HALOGUARDTM IR MONITOR

(OPTIONAL) FOUR or EIGHT POINT SCANNER

INSTRUCTION MANUAL

11285 Elkins Road  Bldg. H-1

Roswell, GA 30076

TEL:  770-667-3865

FAX: 770-667-3857

www.thermalgas.com

IMPORTANT

READ ENTIRE BOOKLET BEFORE

INSTALLING OR OPERATING

HALOGUARDTM IR MONITOR  AND (OPTIONAL) SCANNER

TABLE OF CONTENTS

Page

1.	Unpacking Instructions	3

2.	Before Installation	3

3.	Installation	7

4.	Calibration	10

5.	Testing	10

6.	Trouble Shooting	10

7.	Specifications	11

FIGURES

Page

1.	Dimension Drawing	4

2.	Controller Upper Circuit Board	5

3.	Controller Lower Circuit Board	5

4.	Controller LCD Display Features	6

5.	Infrared (IR) Module Circuit Boards	6

6.	Sensor Cable Terminal Connection	9

7.	Analog Output Jumper and Terminal Settings	7

8.	Function Jumper Settings	8

9.	Initial Factory Settings	11

10.	Exposure Limits	11

11.	Wiring Diagram	12

UNPACKING INSTRUCTIONS

HaloguardTM monitors are carefully packed, inspected and delivered to the carrier in good condition.  If damage occurs in transit it is the responsibility of the carrier.

Carefully inspect the unit upon receipt.  Any damage should be reported to the carrier and an inspection requested.  After inspection by the carrier and your receipt of his acknowledgment as to the damage, contact us for return authorization (RMA).  We cannot file claims for damaged goods on your behalf, but we will assist you in any way we can.

In order to expedite our work, please provide serial number and purchase date when you call.

WE CANNOT ACCEPT RETURNS WITHOUT PRIOR APPROVAL.

BEFORE INSTALLATION

1.	Remove Haloguard Controller and IR Sensor Module from carton.  Check contents against packing list.  If shipment is incomplete, contact us immediately.

2.	The following tools and hardware are required for installation and calibration.

a.	Two standard & one philips screwdrivers; 1 - medium standard w/ long shaft, 1 - jewelers fine standard & 1 - medium philips.

b.	Needle-nosed electrician’s pliers

c. (8) No. 8 x 1” Screw (minimum)

d.	Digital VOM

3.	Select a site for the installation:

a.	Power requirements: Provide a clean source of 115-230 VAC, 50/60 Hz, single phase circuit rated 15A minimum  Haloguard Controller and IR Sensor Module.

b.	Infrared (IR) Sensor Module should be mounted near potential leaks in a quiet area or downstream from leak source in area with air movement.

c.	Infrared (IR) Sensor Module sample tube end should be located 18” - 24” above the floor .  If using optional scanner, locate IR Module at a point central to chiller locations.  Install inlet extension tube out to each remote sample location (up to 200 Ft. from IR module). Make sure each sample tube is equipped with an end of line filter.

d.	Make sure the area selected is not subject to flooding, potential impact or severe ambient temperature and humidity changes (i.e. boiler blow-down or near roll-up doors).

e.	Infrared detector is highly selective but may respond to the presence of other gases (i.e. paint thinner, cleaning fluids and other refrigerants) if interfering gas reaches a high concentration.  For accurate refrigerant leak detection select a location free from above fumes or temporarily disable sensor when they are present.  Contact TGS for specific interference’s.

4.	The wall mounted controller should be installed indoors, approximately five feet above the floor or at a location easily visible to operators, in an area with minimal vibration, and with temperature and humidity changes like sensor location.

IMPORTANT

CONSULT LOCAL AND NATIONAL ELECTRICAL CODES FOR ANY SPECIAL REQUIREMENTS OR RESTRICTIONS BEFORE INSTALLING HALOGUARD.

5.	LED Indicators, Pushbuttons, LCD Displays, and Relays

a.	POWER LED- Green LED indicates Haloguard is receiving AC power.

b.	FAULT LED and Relay - Indicates malfunction. LCD indicates specific type of failure (See Figure 4).

c.	TEST Push-button - Energizes Alarm LED’s & relays.  Depress button five (5) times to sequence through each alarm level.

d.	Adjustable Alarm LEDs & Relays -Indicate Alarm 1&Alarm 2 - Factory set for particular refrigerant (See Figure 9).  User adjustable as follows:

| RANGE | 1 PPM INCREMENTS | 10 PPM INCREMENTS |
| --- | --- | --- |
| 0 - 1000 ppm | 10 - 100 | 100 - 1000 |

Note: 	Optional TWA Integration activates Alarm 1 LED and relay when installed.

TLV-TWA Alarm is factory set and not user adjustable.

e.	OFFSCALE LED and Relay - Factory set at 1000ppm

f.	RESET Push-button - Silences alarm, disables relays, and resets instrument for 20 minutes.  LCD displays *CAUTION* and RESET with 20 minute countdown.  Alarms are automatically reactivated if alarm condition is not corrected.  Reset is automatically initiated on start-up and after power failure (Except when optional UPS is provided.).

6.	Optional Features:

.	TWA Integration - Haloguard calculates an 8 hr. Time Weighted Average (TLV-TWA), displays this value on LCD, activates Alarm 1 LED and relay if factory set PPM value is exceeded. Only used for gases with TLV-TWA less than 1000ppm.

HALOGUARD IR

CONTROLLER

5 1/2”

Figure 1 - Dimensional Drawing

4”

9”

3/4”

HALOGUARD IR

MODULE

6 1/2”

14 1/4”

(By 4” Deep)

RUN

GAS

ALARM

ZERO

SPAN

AUD

J5

VOLT

mA

Offscale LED

Alarm 2 LED

Alarm 1 LED

Power LED

Fault LED

Test Button

UP

ENTER

DOWN

Reset Button

Processor Chip

LCD Brightness

Adjustment

ANALOG

I

C

IR

Trim

Analog Trim Pot

0-5 or 0-10 VDC

Sensor

Connection

RS-232

Setup Jumpers

Scanner Connection

Figure 2 - Controller Upper Circuit Board

1      2      3

4      5      6

10     11    12

7      8      9

ALARM 1

FAULT

OFFSCALE

ALARM 2

Figure 3 - Controller Lower Circuit Board

1

.

.

8

Scanner Circuit Board

(Optional)

Connector for Digital Calibrator (Optional)

Lower Circuit Board

Run

Setup

DO NOT ADJUST POTS

Figure 5 - IR Module Circuit Boards

Cable to Controller

(DO NOT REMOVE)

White

Black

Red

IR Module Run/

Setup Jumper

INSTALLATION

1.	Check power supply. (See Section “Before Installation 3a”)

2.	Disconnect power before beginning.

3.	Installation of Haloguard Controller and  IR Sensor Module

a. To mount Haloguard Controller

1.	Remove Plastic cover.

2.	Install No. 8 x 1” screw (minimum) wall fastener through cover screw holes.

3.	Replace cover.

Refer to figures 2, 3, 4 and 5 before proceeding.

b.	To mount Haloguard IR Sensor Module

1.	Mount IR Module in a VERTICAL position in a location not subject to vibration or extreme temperature or humidity  fluctuation. Install sample tube to 18-24” above floor, install filter.

2.	IR Module Inlet/Exhaust Extension (optional) sample tube may be extended up to 200FT with 0.125” OD x 0.093” ID nylon, copper or stainless steel tubing.  When extending sample tubing:

a.	Keep sample lines as short as possible and free of kinks.

b.	30 micron Inlet Filter should be attached at end of line.

c.	Exhaust to atmosphere.  DO NOT install any device which might restrict the flow.

c.	Wiring Instructions:

1.	Remove cover and face plate from Haloguard Controller and IR Sensor Module using screw driver.

2.	Run cable from Haloguard Controller to IR Sensor Module location.  Eight feet (8FT.) of cable with DIN connectors standard;  optional extension cables are available (Follow instruction in Section 4, Page 9, when extension cables are used).

3.	Relay Terminals - Connect alarm relays (NO or NC) (Figure 3 - Controller Lower Circuit Board) as required.

**WARNING** analog output is a driven signal, do not connect any wire with voltage or 			     current to analog output terminals

4.  Analog Output (Optional) - Connect 18 ga. twisted shielded pair to Controller Upper Circuit Board (Figure 2) as follows:

| Analog Output Range | Terminal Position |
| --- | --- |
| 0-5VDC or 0-10VDC | VDC and COM |
| 4 - 20mA | mA and COM |

Figure 7 - Analog Jumper and Terminal Settings

5. 	Uninteruptable Power Supply (Optional) - Connect Haloguard Controller and IR module to UPS, IR module must be within 10ft. of controller.

d.	On power-up, RESET and 20 minute count down will appear on LCD. For 20 minutes after power up all alarms and relays are automatically disabled.  Whenever power is disrupted, RESET mode will be automatic (unless optional UPS is supplied) to protect against false alarms. Allow 1 hour for warm-up from cold start.

e.	Locate Setup jumpers on Figure 2 - Controller Upper Circuit Board.  Select required settings from the following:

| JP | FUNCTION |
| --- | --- |
| RUN | Select run for normal operation |
| GAS | Set Gas Type |
| ALARM | Alarm 1 and Alarm 2 Set Point Adjustment |
| ZERO | Factory Use Only |
| SPAN | Factory Use Only |
| J5 | Factory Use Only |
| AUD | Audible Alarm Disable |

Figure 8 - Function Jumper Settings

1.	RUN - Remove jumper to initiate Set-Up Mode.  Use jumper to initiate the following set-up modes.  Replace jumper when finished.

2.	GAS - Gas type will be pre-set at the factory (See Figure 9).

3.	Alarm - Alarm levels will be pre-set at the factory.  Scroll through menu to set up Alarm 1 and Alarm 2.  Adjust alarm levels using UP/DOWN and ENTER push-buttons.

4.	ZERO - Factory only.

5.	SPAN - Factory only.

6.	AUD - Local Audible Alarm (optional) is factory installed.  To disable alarm remove “AUD” jumper.

f.	System Configuration:

1.	Relay Setup - Factory setting is Unlatched Mode; e.g., the alarm LEDs and relays will return to a normal status when gas concentration goes below alarm setpoint.  To select Latched Mode place jumper on ALARM setting (Figure 8).  Press TEST button until “LATCH ON” appears on the LCD Display. (LATCH ON mode requires manual RESET of all alarms.)

2.	Analog Output (optional) is factory set at 0 - 5 VDC or 4 - 20mA as ordered. Use Analog trim pot(Figure 2) to adjust for up to 0-10VDC range

3.	LCD display adjustment  changes brightness - Adjust potentiometer (Figure  2).

4.	Four or Eight Point Scanner - (Optional) Scanner is factory installed.  Scanner automatically sequences through each port (1 -4 or 1-8).

A.	Manual Scan - While in RUN Mode,

1.	Press UP or DOWN button on controller.  Each time the button is pressed, display will advance to next/previous sample point. Controller will return to automatic sequencing within 2 minutes.

When changing set-up on scanner, turn power off before proceeding.

B.	Scanner Jumper Setup - Factory setting is for four (4)or eight (8) sample ports.  If 1,2,3,5,6 or 7 sample ports are required, place jumper on corresponding positions located on Scanner Circuit Board(s) in IR Module (Figure 5).  IR Module Scanner will sequence through the selected port settings.

5.	Scan Rate - Scan rate is factory set at 4 seconds per point.  Rate is adjustable from 0 to 10 seconds.  To change scan display rate, from RUN mode at controller, press ENTER and then UP/DOWN to adjust.  Press ENTER to return to RUN mode.

4.	Installation of Haloguard  Controller and IR Sensor Module (Extended Cable Procedure)

Refer to FIGURE 2 - Controller Upper Circuit Board before proceeding.

DO NOT CUT SUPPLIED CABLE

Maximum Extension wire 1000 Feet.

a.	Controller is provided with 18” cable with DIN Connector and sensor is provided with 6-1/2’ cable.  If cable extension is provided by customer, proceed as follows:

We recommend 3 conductor 18 ga. cable with foil shield, Carol C2535 or equal.  Use 3/4” conduit if required.

b.	To extend sensor beyond the provided length, remove 18” cable with DIN connector from controller Upper Circuit Board . Splice or solder extension cable to end of 18” cable.  Reconnect extended sensor cable to terminal block in upper circuit board of controller.

| Terminal | Provided Wire Color | Extension Wire Color | Function |
| --- | --- | --- | --- |
| SCAN | Red | Red | Scanner |
| SIG | White | White | Signal |
| GND | Blk./Blk | Black | Ground |

Note - SCAN Terminal is used with scanner Only.

Figure 6 - Sensor Cable Terminal Connection

To avoid nuisance alarms remove alarm jumper “AUD”  before beginning.

c.	To compensate for line losses adjust signal voltage with a digital VOM as follows:

1.	Open cover on Haloguard IR Module.  Move Jumper from RUN to SETUP  (See Figure 5).  Wait approximately 1 minute before proceeding .

2.	Open cover on Haloguard IR Controller and remove faceplate.

3.	With VOM on 5 VDC scale, place VOM probe on SIG (+) and GND (-) Test points on Controller (see Figure 2).

Adjust potentiometer  “I”  on Controller Upper Circuit Board, with screwdriver until it reads 4.975 +/-0.025  VDC.

Display will show  FAULT  if out of range  and  SETUP , if trimmed to 4.975+/-0.025 VDC.

4.	When done, replace IR Module jumper in  RUN  mode.

5.	Replace AUD jumper to activate alarms circuit.

CALIBRATION

Haloguard IR monitors are factory calibrated to the gas of interest; field recalibration is not required for operation in typical machine room environments during the first twelve months of operation unless drift exceeds more than 5ppm in a 30 day period.

For those who wish to check the factory calibration an optional Digital Calibrator and Span Gas Kit is available. Instructions for use are included with kit

TESTING

The Haloguard IRTM should be tested at start-up, after any changes to alarm protocol, and after each alarm level condition has been corrected. During Testing, display will indicate TEST MODE

a.	Alarm Test - Push TEST button five times to check all alarm levels sequentially.  Alarm relays, lights, audible and remote alarms (if equipped) will activate.

b.	Reset Test - Push RESET/SILENCE button; alarm relays, audible and remote alarms (if equipped) will become inactive for 20 minutes.  Display will read  RESET  and indicate minutes to completion of reset period.

TROUBLESHOOTING

The most frequent cause of nuisance alarms and faults is improper set-up, primarily due to:

a.    Failure to install in accordance with instructions.

b.	Not allowing sufficient warm-up time.

c.	Poor sensor location.

To check Zero Calibration, fill a clean plastic trash bag with clean outside air, tie off  with twist-tie, let sample stabilize inside for 15 - 20 minutes.  Insert sample tube into bag . For models equipped with scanner allow up to 2.5 minutes per channel for clean air sample analysis

.

Observe LCD response, if dispalyed PPM value drops lower then Haloguard IR is detecting the presence of the gas of interest or another gas which absorbs IR light at the same frequency.

Remove sample tube from bag and observe LCD response. If displayed PPM value  moves higher, look for refrigerant leaks or possible sources of interfering gases  (See “Before Installation” section 3e). and relocate sensor. Keep in mind that the Haloguard IR is much more sensitive than hand held leak detectors, it may detect a leak when  hand held units  show no response

We wish to aid with any  problems you might experience with the Haloguard IR.  When contacting Thermal Gas Systems, Inc. Service Department, please have the following information ready

1.	Model Number and Serial Number.

2.	Description of problem.

3.	Remoce faceplate. Place jumper on Alarm setting function.and record settings.

4.	Measure voltage between SIG and GND.(Fig. 2) in SETUP and RUN modes  Write down values

5.	Advise the condition of all LED’s and all information displayed on the LCD.

SPECIFICATIONS

Technology:	Photoacoustic Infrared

Electrical Supply:	115-230 VAC, 50-60Hz

Output Signal:	Std.  4 x  3A Dry Contact Relays

(either NO or NC)

Analog Output	Opt.  0 - 5 VDC or 4 - 20mA

Alarm Outputs:	Three Level Contact Closure

Readout:	Digital Meter, Displayed in PPM

Gas Type, Range and Options

Display accuracy:	1ppm      0 - 100 ppm Range

10ppm   100 - 1000 ppm Range

Ranges:	0 - 1000 ppm   R-11,R- 12, R-22,        			R123, R-134a,

Response Time:	< 1 Minute single point

< 2.5 Minutes per point with optional 	scanner.

Operating Conditions:

IR Module	+40oF to +110oF Non-condensing

Controller	 0oF to +120oF Non-condensing

Fault Diagnostics:	Indicator Light or LCD Readout for

fault diagnostics See Figure 5)

Materials:

IR Module	NEMA 4/12/13 IP 65 Design

Controller	NEMA 4/12/13, IP65 Design

Weight:

IR Module	10 lbs.

Controller:	4 lbs

Dimensions:

IR Module	6-1/2” W x 14-1/4” H x 4” D

Controller	5- 1/2” W x 9” H x 4”D

Initial factory settings are:

| Function | Setting |
| --- | --- |
| Gas |  |
| Alarm 1 |  |
| Alarm 2 |  |
| Full Scale PPM |  |
| TWA Alarm Level |  |

Figure 9 - Initial Factory Settings

| GAS | TLV-TWA* | CEIL | PEL |
| --- | --- | --- | --- |
| R-11 |  | 1000 |  |
| R-12 | 1000 |  | 1000 |
| R-22 | 1000 |  | 1000 |
| R-123 | 50 |  |  |
| R-134a | 1000 |  | 1000 |

Other exposure limits are pending.

TLV-TWA = 8hr./day, 40hr./wk. avg.  Short term exposures should not exceed 3 - 5 times the TWA for more than 30 min./day.

* ACGIH Trademark.

Figure 10 - Exposure Limits

WARNING

Analog output lines must not be connected to any kind of voltage or current source, serious damage will result.

(OPTIONAL)

STROBE LIGHT

Line Cord

115 VAC 50/60Hz.

AC HOT

AC COMM commonCOMMON

GROUND

G

N

L

Green

White

Black

1

3

2

4

6

5

7

9

8

10

12

11

2

3

4

5

6

7

8

9

10

11

12

ALARM

1

FAULT

OFFSCALE

ALARM

2

Notes:

1. Power Cord - Provided w/ wall plug connector and 8 Ft. 3 conductor wire.

2. Optional Audible Alarm factory wired.  Remote Audible and Visual Alarms

must be 120VAC and connected to terminal in Junction Box.

3.  Sensor Cable Use, 3 conductor 18 or 20ga. w/ foil shield.

4. Analog Outputs are either 0 - 5VDC or 0 - 10VDC.

8’ Cable w/ DIN Plug in Connector

IR SENSOR MODULE

ALL WIRES COMING INTO IR SENSOR MODULE ARE HARD WIRED.

S

G

S

Used only with Scanner (Optional)

Cable from Controller

Lower Circuit Board

ANALOG OUTPUTS

TO BAS OR OTHER

+V S G

Haloguard IR  Controller

Upper Circuit Board

(OPTIONAL)

AUDIBLE ALARM

+  A  +  L

See Chart for Connection

S G

Notes:

1.  Power Cord - Provided w/ wall plug connector and 8 Ft. 3 conductor wire.

2.  Audible and Visual Alarm (Optional) factory wired.  Remote Audible and Visual Alarms

must be 120VAC and connected to terminal Strip on Lower Circuit Board.

3.  Sensor Cable between Haloguard IR Controller and IR Sensor Module - Maximum Length 1000FT. Use,

3 conductor 18 or 20ga. w/ foil shield.

4.  Analog Outputs (Optional) are either 0 - 5 to  10VDC, and 4 - 20mA.

5.  If  Optional scanner is installed, Red wire is connected to scanner terminal on upper circuit board.

Green

Line Cord

115 VAC 50/60Hz.

AC HOT

GROUND

G

N

L

White

Black

Cable Color Code

White - S     Signal

Black - G     Ground

Red - Scan   Scanner(Only)

Figure 11 - Wiring Diagram

Plug in DIN Connector

AC COMMON

(3) Cable to

IR Sensor Module