IR SENSOR MODULE

Line Cord

115 VAC 50/60Hz.

AC HOT

ACCOMMON

GROUND

G

N

L

Green

White

Black

ALL WIRES COMING INTO IR SENSOR MODULE ARE HARD WIRED.

S

G

Cable from Controller

VIS

-     +

2    1

AN1

+     -

1    2

AN2

+     -

1    2

AN3

+     -

1    2

AN4

+     -

1    2

AUD

-     +

2    1

G

N

L

1   NC

2   COM

3   NO

4   NC

5   COM

6   NO

7   NC

8   COM

9   NO

10  NC  11  COM

12  NO

1

2

3

4

5

6

7

8

9

10

11

12

CHANNEL 1

+V S G

1  2  3

CHANNEL 2

+V S G

1  2  3

CHANNEL 3

+V S G

1  2  3

CHANNEL 4

+V S G

1  2  3

CHANNEL 5

+V S G

1  2  3

CHANNEL 6

+V S G

1  2  3

WARNING

Analog output lines must not be connected to any kind of voltage or current source, serious damage will result.

Wiring Diagram

Notes:

1. Power Cord - Provided w/ wall plug connector and 8 Ft., 3-conductor wire.

2. Optional Audible Alarm factory wired.  Remote Audible and Visual Alarms

must be 120VAC and connected to terminal in Relay Junction Box.

3.  Sensor Cable Use, 3 conductor 18 or 20ga. w/ foil shield.

4. Analog Outputs are either 0 - 5VDC or  0 - 10VDC.

8’ Cable w/ DIN Plug in Connector

(Typical for up to six (6) Sensors

IR Sensor Module, CMOS, or Oxygen)

ANALOG OUTPUTS

TO BAS OR OTHER (Typical 4)

Line Cord

115 VAC 50/60Hz.

AC HOT (Black)

AC COMMON (White)

GROUND (Green)

(OPTIONAL)

AUDIBLE ALARM 12VDC

OFFSCALEEEEE

HI ALARM

LOW ALARM

FAULT

(OPTIONAL) STROBE ALARM

12VDC

Cable to

IR Sensor Module

Haloguard II Controller