HALOGUARD™ III

# MULTI-POINT, MULTI-GAS MONITOR

INSTRUCTION MANUAL

11285 Elkins Road  Bldg. H-1

Roswell, GA 30076

TEL:  770-667-3865

FAX: 770-667-3857

www.thermalgas.com

****IMPORTANT****

USER TO READ, FULLY UNDERSTAND AND FOLLOW ALL INSTRUCTIONS PROVIDED BY THE MANUFACTURER FOR INSTALLATION AND OPERATION OF THE HALOGUARDTM III MONITOR. FAILURE TO DO SO COULD RESULT IN HARM.

TABLE OF CONTENTS

Page

1.	Unpacking Instructions	3

2.	Before Installation	3

3.	Function of LED’s, Pushbuttons, & LCD Information	4

4.	Installation	6

5.	Set-up & System Configuration	8

6.	Calibration, Testing, & Trouble Shooting	10

7.	Maintenance & Specifications	11

FIGURES

Page

1.	Typical Area Monitoring Installation  		3

2.	Mounting Dimensions		4

3.	LCD Display Information		4

4.	HaloguardTM III		5

5.	Analog Jumper Settings		6

6.	Circuit Board (Shown with Optional 8 Point Scanner)		7

7.	Setup & Configuration Jumper Settings		8

8.	Remote Expansion Module Terminations		9

9.	Remote Expansion Module Circuit Board		9

10.	Replacement Parts		11

11.	Accessories		11

12.	Initial Factory Settings		11

13.	Refrigerant Exposure limits		11

14	Wiring Diagram		12

15	APPENDIX A  - Analog Output Data Translation		13

UNPACKING INSTRUCTIONS

HaloguardTM monitors are carefully packed, inspected and delivered to the carrier in good condition.  If damage occurs in transit it is the responsibility of the carrier.  Carefully inspect the unit upon receipt.  Any damage should be reported to the carrier and an inspection requested.  After inspection by the carrier and your receipt of his acknowledgment as to the damage, contact us for return authorization (RMA).  We cannot file claims for damaged goods on your behalf, but we will assist you in any way we can.  In order to expedite our work, please provide serial number and model number when you call.

WE CANNOT ACCEPT RETURNS WITHOUT PRIOR APPROVAL.

BEFORE INSTALLATION

1.	Remove HaloguardTM III from carton.  Check contents against packing list.  If shipment is incomplete, contact us immediately.

2.	Select a site for the installation:

a.	Power requirements: Provide a clean source of power 115-230 VAC, 50/60 Hz, single phase 15A minimum.

b.	Sample tube pick-up should be located near potential leaks in a quiet area or downstream from leak source in area with air movement.

c.	Sample tube pick-up should be located 18” - 24” above the floor.  If using optional scanner, locate sample tubes at points near all chiller locations.  Make sure each sample tube is equipped with an end of line filter.

d.	Make sure the area selected is not subject to flooding, potential impact or severe ambient temperature and humidity changes (i.e. boiler blow-down or near roll-up doors).

- Wide band infrared detector is non-selective and may respond to the presence of other gases (i.e. paint thinner, cleaning fluids and other refrigerants) if interfering gas reaches a high concentration.  For accurate refrigerant leak detection select a location free from above vapors or temporarily disable sensor when they are present.  Contact us for specific gas interference.

3.  	The HaloguardTM III should be installed indoors, about five feet above the floor and at a location easily visible to operators, in an area with minimal vibration, and with temperature and humidity changes like sample pick-up location.  DO NOT MOUNT DIRECTLY TO CHILLER

Remote Alarm

Refrigerant Storage Area

Sample point

Sample point

Sample point

HaloguardTM

Panel and Local Alarm

Fan

Chillers

Remote Alarm

## Fig. 1-Typical Area Monitoring Installation

LCD Brightness

Adjustment

IMPORTANT

CONSULT LOCAL AND NATIONAL ELECTRICAL CODES FOR ANY SPECIAL REQUIREMENTS OR RESTRICTIONS BEFORE INSTALLING HALOGUARDTM.

# FUNCTION OF LED’S, PUSHBUTTONS, and LCD DISPLAY INFORMATION

1.	READY LED- Steady LED means HaloguardTM III is measuring ppm; blinking indicates otherwise.

2.	POWER LED – Indicates HaloguardTM III is receiving power.

3.	FAULT LED – Indicates malfunction. LCD displays specific type of failure (See Figure 3)

- ALARM 1, ALARM 2, ALARM 3 LED’s - Adjustable Alarm levels & relays - Factory set for particular refrigerant (See Figure 12 ).  User adjustable as follows:

| MEASURMENT RANGE | 1 PPM INCREMENTS | 10 PPM INCREMENTS |
| --- | --- | --- |
| 0 - 1000 ppm | 50 – 100 ppm | 100 – 1000 ppm |

- MANUAL SCAN push-button – Allows manual scan of last ppm reading for all channels.

6.	RESET/SILENCE push-button - Silences alarms, disables relays, and resets instrument for 20 minutes.  LCD displays RESET/SILENCE with 20-minute countdown.  Alarms are automatically reactivated if alarm condition is not corrected.  Reset is automatically initiated on start-up and after power failure.

Alarms

- Alarm 1

- Alarm 2

- Alarm 3

- Reset

- Fault

- Silenced

Set-up Messages

- Set Channel (1-24)

- Set Gas Type (R11,12,22,123,134)

- Set Scan Rate: (1-10 seconds)

- Test Alarm 123456 Fault

- Set Alarm 123456 Latch On/Off

Calibration Messages

- Zero Calibrate, connect scrubber,

(Follow on screen directions)

- Span Calibrate, insert Span Key (from gas cal kit

Figure 3 - LCD Display Features

8 hr. TWA ppm (R-123 )

Fault Messages

- Chopper Failure

- Discontinuity

- Lamp Failure

- Low Temperature

- Flow Failure

- Scanner Stop

- Remote EE Error

- Channel Error

Gas Type (R-11, R-12, R-22, R-123, R-134, etc.)

Channels 1 - 24 (Opt. Scanner Only)

Concentration

(ppm)

7.	Optional Display Features: TWA Integration – HaloguardTM III calculates an 8 hr. Time Weighted Average (TLV-TWA), displays this value on LCD, activates Alarm 1 LED and relay if factory set PPM value is exceeded. Used for gases with TLV-TWA less than 1000ppm. TLV-TWA Alarm is factory set and not user adjustable.

11”

Fig. 2- Mounting Dimensions

14 3/4”

Sample Inlet

1 inlet Std.

2,4,8 inlet Opt.

Inlet can be extended 300’ using 0.125”  tubing. All lines must have end of line filter.

Remote Reset In

Analog/ Digital Output

4-20mA, 0-5VDC –Opt

RS 232/485 serial Opt.

Relay/Binary Output

4x5A. Dry Contact Std

7x10A. Dry Contact Opt.

Power In

120/230Vac

50/60Hz

Reset/Silence

Pushbutton

Test Pushbutton

Enclosure is 12” x 14” x 4.5”; NEMA 12

LCD

Local Strobe Alarm – Opt.

Local Audible alarm - Opt.

Mounting Holes

(4) 0.25”dia.

Ready

Power

Fault

Alarm 3

Alarm 2

Alarm 1

Aux. Inputs and Remote Expansion Module In

Fig. 4-Haloguard III Layout

Sample

Outlet

INSTALLATION

1.	Check power supply and determine best location. (See Section “Before Installation”)

2.	Disconnect power before beginning.

Refer to figures 2, 3, 4, 5, 6, and 14 before proceeding.

3.	Installation

a.	Mounting HaloguardTM III

1.	Securely mount the unit to a wall or support using the (4) mounting holes.

2.	Remove cover.

3.	Install sample tube to 18-24” above floor, install end of line filter. Sample inlet may be extended up to 300FT with 0.125” OD x 0.093” ID nylon, copper or stainless steel tubing.  When extending sample tubing:

a.	Keep sample lines as short as possible and free of kinks.

b.	Exhaust to atmosphere.  DO NOT install any device that might restrict the flow.

- Route sample inlet tubing through entry indicated (Figure 4) and insert into one-touch fitting provided. To remove tubing pull plastic ring on end of one-touch fitting to release.

b.	Wiring Connections:

- Relay Terminals – Route wire through entry indicated. (Figure 4). Remove safety cover. Connect alarm relays NO or NC (Figure 14) as required.

- Power Supply Wiring-Route wire through entry indicated. (Figure 4). Remove safety cover.  All connections are made to the terminal block labeled IN 120/250VAC (Figure 14). Connect HOT AC wire to Terminal L. Connect NEUTRAL wire to terminal N. Connect a GROUND wire to terminal G.  Auxiliary 120/250VAC output is provided to activate remote audible and strobe light alarms. This output is not fused.  Limit load to 0.5A.max total.  Replace cover.

**WARNING** analog output is a driven signal, do not connect any wire with voltage or 			     current to analog output terminals

- Analog Output (Optional) – Two analog outputs are provided for connection to remote recording devices;  PPM ANALOG OUTPUT is for gas concentration;  CHANNEL ANALOG OUTPUT is for channel location (Figure 14). Connect 18 gage twisted shielded pair as follows, maximum length 300 ft.:

| Analog Output Range | Terminal Position |
| --- | --- |
| 0-10VDC | V and GND |
| 4 - 20mA | I and GND |

Figure 5  - Analog Output Terminal Block Settings

- External Input (VDC)  – Five analog inputs (EXT INPUT 1-5) are provided for connection of remote input devices such as oxygen sensors, CO sensors, and flammables sensors (Figure 6).

- Remote Input (mA)  – Two analog inputs (REMOTE IR INPUT 1 & 2) are provided for connection of HaloguardTM Remote Expansion Module (Figure 6). Each terminal block has connections for both Remote channel and PPM inputs.

- Uninterruptible Power Supply  (Optional) – Make sure UPS is fully charged. Plug UPS into power supply, turn switch ON. Connect HaloguardTM III to UPS, with power cord provided.

EXHAUST

CELL COVER

DRAW PUMP

(UNDER PC BOARD)

CAUTION

Do not remove this cover

Trained service personnel only

No user serviceable components inside

CONNECTORS

3      4      5      6      7      8

CONNECTOR 1

LCD DISPLAY

8-PORT SCANNER BLOCK

1      2      3      4       5      6      7      8

INLET PORTS

AIR FILTER

TEST SAMPLE

INLET TUBE

On power-up, RESET/SILENCE and 20 minute count down will appear on LCD. For 20 minutes after power up all alarms and relays are automatically disabled.  Whenever power is disrupted, RESET/SILENCE mode will be automatic (unless optional UPS is supplied) to protect against false alarms. Allow 1 hour for warm-up from cold start.

Figure 6 Circuit Board

(Shown with Optional 8 Point Scanner)

SETUP and SYSTEM CONFIGURATION

Locate jumpers on Figure 6.  Select configuration settings from the following:

| JP | # FUNCTION |
| --- | --- |
| RUN | Select run for normal operation |
| SETUP | Set gas type and number of active channels |
| TEST | Sequentially activates all Alarm & Fault LED’s & relays |
| ALARM | Set-point Adjustment for Alarm 1, 2, and 3. Latch ON/OFF |
| CAL | Zero Calibration |
| SPAN | For use only with span gas and key |
| JP5 | Factory only |

Figure 7 – Setup & Configuration Jumper Settings

1.	RUN – Normal operation jumper position.  Replace jumper when finished other modes.

- SETUP – Gas types and number of active channels will be preset at the factory (Figure 12).  To change gas type or activate a channel, first select the channel to activate with cursor using the UP and DOWN pushbuttons. Press ENTER then use the same pushbuttons to select the gas type for each channel. Be sure to press ENTER to select. “NONE” selected in the gas type menu will deactivate the channel.

- TEST- Select alarm to test with cursor by using the UP, DOWN, and ENTER pushbuttons.

4.	ALARM –Alarm levels will be preset at the factory (Figure 12). Select the ALARM to adjust with the cursor using the UP, DOWN, and ENTER pushbuttons. Use the same pushbuttons to change the alarm PPM set-point. “OFF” selected turns alarm off.

5.	CAL – Install optional activated charcoal filter on channel 1; follow on screen directions for zero calibration using the ENTER pushbutton.

6.	SPAN –Key and instructions for use are included with optional Span Gas Calibration Kit

7.	JP5- Factory only.

System Configuration:

1.	Relay Latch Setup - Factory recommended setting is unlatched mode; e.g., the alarm LED’s and relays will return to a normal status when gas concentration goes below alarm set-point.  To select latched mode place jumper on ALARM setting.  Select LATCH mode with the cursor using the UP, DOWN, and ENTER pushbuttons. LATCH ON appears on the LCD Display. Latched mode requires manual RESET for all alarms

2.	Analog Output (optional) is factory set at 0-5VDC or 4-20mA as ordered. Use Analog trim pot (Figure 6) to adjust voltage for up to 0-10VDC range

3.	LCD display adjustment potentiometer changes brightness (Figure 6).

4.	Two, Four, or Eight Point Scanner - (Optional) Scanner is factory installed.  Scanner automatically sequences through each active port (1-2, 1-4 or 1-8).

a.	Manual Scan - While in RUN Mode,

- Press MANUAL button on side of controller.  Each time the button is pressed, display will advance to next sample point. Controller will return to automatic sequencing within 2 minutes.

- Adjust Scan Display Rate - Rate is factory set at 4 seconds per point. Rate is adjustable from 1-10 seconds. To change scan display rate press ENTER from RUN mode; adjust using UP and DOWN; press ENTER to return to RUN mode.

INSTALLATION OF OPTIONAL REMOTE IR EXPANSION MODULE

Refer to FIGURE 4, 6, 8, 9 and 14 before proceeding.

DO NOT CUT SUPPLIED CABLE

Controller is provided with 18” cable with DIN connector and expansion module is provided with 6-1/2’ cable.  If cable extension is required we recommend 3-conductor, 18-gage cable with foil shield, Carol C2535 or equal.  Use 3/4” conduit if required.  Maximum length - 1000 ft.

Remove 18” cable with DIN connector from controller circuit board terminal block marked REMOTE INPUT 1(or REMOTE INPUT 2). Splice or solder extension cable to end of 18” cable.  Reconnect extended sensor cable to terminal block on circuit board of controller.

| Terminal | 18” cable Wire Color | Extension Wire Color | Remote Function |
| --- | --- | --- | --- |
| CHA | Red | Red | Scanner |
| SIG | White | White | Signal |
| GND | Blk/Blk | Black | Ground |

Note - CHA Terminal is used for expansion modules with scanner only.

# Figure 8 – Remote Expansion Module Terminal Connection

To avoid nuisance alarms remove “AUD” alarm jumper in HaloguardTM III before beginning.

To compensate for line losses adjust signal voltage with a digital VOM as follows:

1.	Open cover on Remote IR expansion module.  Move jumper from RUN to SETUP.  Wait approximately 1 minute before proceeding. (Display of HaloguardTM III shows SETUP.)

2.	Open cover on HaloguardTM III. Controller

3.	With VOM on 5 VDC scale, place VOM probe on SIG (+) and GND (-) Test points on HaloguardTM III Main Board (Figure 6). Adjust ADJ1 or ADJ2 potentiometer with screwdriver until it reads 4.975 +/- 0.025 VDC.

4. 	If Remote expansion module is provided with scanner, lock the scanner on channel 1 using the jumper provided (Figure 9) on the Scanner Circuit Board.  With VOM on 5 VDC scale, place VOM probe on CHA (+) and GND (-) Test points on HaloguardTM III Main Board (see Figure 6). Adjust ADJ4 or ADJ5 potentiometer with screwdriver until it reads 1.0 +/- 0.05 VDC.

5.	Move scanner channel jumper in expansion module back to its original position.

6.	Move jumper in expansion module back to RUN. Replace AUD jumper in HaloguardTM III.

Lower Circuit Board

IR Module Run/

Setup Jumper

DO NOT ADJUST POTS

Figure 9 - Expansion Module Circuit Board

Cable to Controller

(DO NOT REMOVE)

Digital Calibrator Connector Pins

Scanner Circuit Boards

Red

White

Black

RUN

J2

SETUP

1         4

Scanner Channel Jumper

CALIBRATION

HaloguardTM III monitors are factory calibrated to the primary gas of interest.  Field calibration is not required for operation in typical machine room environments during the first twelve months of operation unless a change in gas type is required

For those who wish to check the factory calibration or change the gas type an optional Span Gas Kit is available. Instructions for use are included with kit

TESTING

The HaloguardTM III should be tested at start-up, after any changes to alarm protocol, and after each alarm level condition has been corrected. During testing, display will indicate ALARM TEST

a.	Alarm Test – Enter TEST mode with jumper, select alarm with cursor by using the UP, DOWN, and ENTER pushbuttons.  Check all alarms sequentially.  Alarm relays, lights, audible, analog outputs, and remote alarms (if equipped) will activate if selected.

b.	Reset Test - Push RESET/SILENCE button; alarm relays, audible and remote alarms (if equipped) will become inactive for 20 minutes.  Display will read RESET/SILENCE and indicate minutes to completion of reset period.

###### TROUBLESHOOTING

The most frequent cause of nuisance and fault alarms is improper set-up, primarily due to:

a.	Failure to install in accordance with instructions.

b.	Not allowing sufficient warm-up time.

c.	Poor sensor location.

To check Zero Calibration, fill a clean plastic trash bag with clean outside air, tie off with twist-tie, let sample stabilize inside for 15 - 20 minutes.  Insert sample tube into bag. For models equipped with scanner allow up to 2.5 minutes per channel for clean air sample analysis.

Observe LCD response, if displayed PPM value changes to near 0 PPM, the HaloguardTM III is detecting the presence of the gas of interest or another gas in the room which absorbs infrared light at the same frequency.

Remove sample tube from bag and observe LCD response. If displayed PPM value moves higher, look for refrigerant leaks or possible sources of interfering gases (See “Before Installation”) and relocate sample point. Keep in mind that the HaloguardTM III is much more sensitive than hand held leak detectors, it may detect a leak when hand held units show no response.

We wish to aid with any problems you might experience with the HaloguardTM III.  When contacting Thermal Gas Systems, Inc. Service Department, please have the following information ready:

1.	Model Number and Serial Number.

2.	Description of the problem.

3.	Remove cover. Place RUN jumper on ALARM and record settings. Place jumper on SETUP and record settings. Place jumper on JP5 and record settings.

4.	Advise the condition of all LED’s and all information displayed on the LCD.

MAINTENANCE

There is no scheduled maintenance for the first 12 months operation; after 12 months the internal and external filters should be changed and the instrument should be gas tested in accordance with the instructions. Self-diagnostics will indicate the cause of any unusual malfunction.  To obtain spare or replacement parts please contact Thermal Gas Systems, Inc.

| Description | Part No. |
| --- | --- |
| Internal Filter, element | A702 |
| External Filter, element | A703 |
| Switcher Valve | A501 |
| Pressure Switch | A708 |
| Scanner, 2-station | A501 |
| Scanner, 4-station | A502 |
| Scanner, 8-station | A503 |
| Power Supply; 120/230VAC | A707 |
| Vacuum Pump | A709 |

Figure 10 – Replacement Parts

| Description |  | Part No. |
| --- | --- | --- |
| Audible alarm, local | A603 |  |
| Strobe alarm, local | A607 |  |
| Audible alarm, remote | A605 |  |
| Strobe alarm, remote | A606 |  |
| Combination audible/strobe alarm, | A604 |  |
| Zero Gas Scrubber |  |  |
| Span Gas Kit | A204 |  |

Fig. 11- Accessories

SPECIFICATIONS

Technology:	Wide band Photoacoustic Infrared

Electrical Supply:	115-230 VAC, 60Hz, 65W

Fuse:	3A / 240V; Fast Acting

Output Signal:	Std.  4x3A Dry Contact SPDT

Opt. 7x10A. Dry Contact SPDT

Analog Output	Opt.  0 – 5/10 VDC or 4 - 20mA

Opt. RS232/485 Serial

Alarm Outputs:	Std. Three Level Contact Closure

Opt. Seven Level Contact Closure

Readout:	Digital LCD; Displays Channel, PPM	Gas Type, and Fault Diagnostics

Display accuracy:	1ppm      10 - 100 ppm Range

10ppm   100 - 1000 ppm Range

Range:		50 - 1000 ppm   R-11, 12, 22, 123, 134a

Operating Conditions:

+40oF to +120oF Non-condensing

Fault Diagnostics:	Indicator LED and LCD Readout

(See Figure 5)

Enclosure: 	NEMA 12 Std. NEMA 4 Optional

Weight: 	23 lbs.

Dimensions: 	12” W x 14” H x 4.5” D

Sample Rate 	1.0 Liter/min.

Response Time:	< 1 Minute per point

< 2.5 Minutes per point with optional 	scanner.

| GAS | TLV-TWA* | CEIL | PEL |
| --- | --- | --- | --- |
| R-11 |  | 1000 |  |
| R-12 | 1000 |  | 1000 |
| R-22 | 1000 |  | 1000 |
| R-123 | 50 |  |  |
| R-134a | 1000 |  | 1000 |

| Channel | # Gas Type |
| --- | --- |
| 1 |  |
| 2 |  |
| 3 |  |
| 4 |  |
| 5 |  |
| 6 |  |
| 7 |  |
| 8 |  |

| ALARM | PPM: |
| --- | --- |
| # 1 |  |
| # 2 |  |
| # 3 |  |
| # 4 |  |
| # 5 |  |
| # 6 |  |

##### Figure 12 - Initial Factory Settings

### Figure 13- Refrigerant Exposure limits

WHITE

GREEN

BLACK

LINE CORD

120/ 250 VAC 50/ 60 HZ

CELL COVER

DRAW PUMP

(UNDER PC BOARD)

CAUTION

Do not remove this cover

Trained service personnel only

No user serviceable components inside

CONNECTORS

3      4      5      6     7      8

LCD DISPLAY

8-PORT SCANNER BLOCK

1      2      3      4      5      6      7      8

INLET PORTS

AIR FILTER

TEST SAMPLE

INLET TUBE

RELAY

RELAY

RELAY

RELAY

OPTIONAL RELAYS

TERMINALS FOR EXTERNAL DEVICE

(NOT FUSED)

EXHAUST

OXYGEN SENSOR CONNECTIONS

(OPTIONAL)

ANALOG OUT

(OPTIONAL)

IR

REMOTE MODULE CONNECTIONS

(OPTIONAL)

WHITE

BLACK

RED

WHITE

BLACK

RED

CONNECTOR 1

Figure 14 Wiring Diagram

APPENDIX  A

# ANALOG OUTPUT DATA TRANSLATION

PPM & FAULT DATA VALUES

To calculate the analog outputs of the display value (PPM) use the following formulas.

For Voltage out:		Vout = ((PPM*56) +3277) * 7.629E-05

For Current out:		Iout = ((PPM*56) +3277) * 2.441E-04

Display PPM values:

| ## PPM | Vout (V) | Iout (mA) | Vterminated* |
| --- | --- | --- | --- |
| 0 | 0.25 | 4.80 | 1.20 |
| 100 | 0.68 | 6.17 | 1.54 |
| 200 | 1.10 | 7.53 | 1.88 |
| 300 | 1.53 | 8.90 | 2.23 |
| 400 | 1.96 | 10.27 | 2.57 |
| 500 | 2.39 | 11.64 | 2.91 |
| 600 | 2.81 | 13.00 | 3.25 |
| 700 | 3.24 | 14.37 | 3.59 |
| 800 | 3.67 | 15.74 | 3.93 |
| 900 | 4.10 | 17.10 | 4.28 |
| 1000 | 4.52 | 18.47 | 4.62 |

Display Fault values:

| #### Fault | Vout (V) | Iout (mA) | Vterminated* |
| --- | --- | --- | --- |
| ##### Remote Discontinuity | 0.000 | 4.00 | 1.00 |
| Offscale | 4.575 | 18.64 | 4.66 |
| Pump Failure | 4.675 | 18.96 | 4.74 |
| Low Temperature | 4.725 | 19.12 | 4.78 |
| Lamp Failure | 4.775 | 19.28 | 4.82 |
| Chopper Failure | 4.825 | 19.44 | 4.86 |
| Scanner Stopped | 4.875 | 19.60 | 4.90 |
| Remote Channel Error | 4.925 | 19.76 | 4.94 |
| Remote In Setup | 4.975 | 19.92 | 4.98 |

* Voltage resulting from termination of Current out with a 250 Ohm resistor.

# ANALOG OUTPUT DATA TRANSLATION

CHANNEL DATA VALUES

| Channel | Voltage (V) | Current (mA) | Vterminated* |
| --- | --- | --- | --- |
| 1 | 0.20 | 4.64 | 1.16 |
| 2 | 0.40 | 5.28 | 1.32 |
| 3 | 0.60 | 5.92 | 1.48 |
| 4 | 0.80 | 6.56 | 1.64 |
| 5 | 1.00 | 7.20 | 1.80 |
| 6 | 1.20 | 7.84 | 1.96 |
| 7 | 1.40 | 8.48 | 2.12 |
| 8 | 1.60 | 9.12 | 2.28 |
| 9 | 1.80 | 9.76 | 2.44 |
| 10 | 2.00 | 10.40 | 2.60 |
| 11 | 2.20 | 11.04 | 2.76 |
| 12 | 2.40 | 11.68 | 2.92 |
| 13 | 2.60 | 12.32 | 3.08 |
| 14 | 2.80 | 12.96 | 3.24 |
| 15 | 3.00 | 13.60 | 3.40 |
| 16 | 3.20 | 14.24 | 3.56 |
| 17 | 3.40 | 14.88 | 3.72 |
| 18 | 3.60 | 15.52 | 3.88 |
| 19 | 3.80 | 16.16 | 4.04 |
| 20 | 4.00 | 16.80 | 4.20 |
| 21 | 4.20 | 17.44 | 4.36 |
| 22 | 4.40 | 18.08 | 4.52 |
| 23 | 4.60 | 18.72 | 4.68 |
| 24 | 4.80 | 19.36 | 4.84 |

* Voltage resulting from termination of Current out with a 250 Ohm resistor.