+

-

(Optional)

BATTERY

BACK-UP

Plug in Molex Connector

Notes:

1. 8’ Power Cord w/ wall plug connector provided.

2. Local Audible /Strobe factory wired.  Remote Audible and Visual Alarms

must be 120VAC and connected to terminal in Relay Junction Box.

3.  Sensor Cable is 3 conductor 18. w/ foil shield.

4. Analog Outputs are adjustable 0 - 5VDC or  0 - 10VDC.

8’ Cable w/ DIN Plug in Connector provided for each sensor

(Typical for up to six (6) Sensors

CMOS refrigerant or Oxygen)

MAXIMUM WIRE LENGTH 300 FT.

(OPTIONAL)

AUDIBLE ALARM

(OPTIONAL)

STROBE ALARM

12VDC

ANALOG OUTPUTS

TO BAS OR  OTHER (Typical of 4)

Outputs

(4) relay

contacts

OFFSCALE		POWER

HI ALARM		TEST

LO ALARM		ZERO

FAULT			MAN

RESET			RESET

PPM-%O2

Haloguard II Controller

Locate sensor 18-24” AFF

Line Cord

120-230 VAC

50/60Hz