HALOGUARDTM II

MULTI-GAS  MULTI-SENSOR MONITOR

INSTRUCTION MANUAL

11285 Elkins Road  Bldg. H-1

Roswell, GA 30077

TEL:  770-667-3865

FAX: 770-667-3857

www.thermalgas.com

IMPORTANT

READ ENTIRE BOOKLET BEFORE

INSTALLING OR OPERATING

HALOGUARDTM II MONITOR

TABLE OF CONTENTS

Page

1.	Unpacking Instructions	3

2.	Before Installation	3

3.	Installation	6

4.	Calibration	7

5.	Testing	9

6.	Trouble Shooting	9

7.	Specifications	10

FIGURES

Page

1.	Dimension Drawing	4

2.	Upper Circuit Board	4

3.	Lower Circuit Board	5

4.	Junction Box Relay Connections	5

5.	LCD Display Features	5

6.	Terminal Connectors	6

7.	Function Jumper Settings	7

8.	Alarm Jumper Settings	8

9.	Exposure Limits	8

10.	Initial Factory Settings	10

11.	Wiring Diagram	11

UNPACKING INSTRUCTIONS

HaloguardTM monitors are carefully packed, inspected and delivered to the carrier in good condition.  If damage occurs in transit it is the responsibility of the carrier.

Carefully inspect the unit upon receipt.  Any damage should be reported to the carrier and an inspection requested.  After inspection by the carrier and your receipt of his acknowledgment as to the damage, contact us for return authorization (RMA).  We cannot file claims for damaged goods on your behalf, but we will assist you in any way we can.

In order to expedite our work, please provide serial number and purchase date when you call.

WE CANNOT ACCEPT RETURNS WITHOUT PRIOR APPROVAL.

BEFORE INSTALLATION

1.	Remove HaloguardTM from carton.  Check contents against packing list.  If shipment is incomplete, contact us immediately.

2.	The following tools and hardware are required for installation and calibration.

a.	Two standard screwdrivers; 1 - medium, 1 - jewelers fine.

b.	Needle-nosed electrician’s pliers

c.	9/32” Nut driver

d. (3) No. 10 x 1” Screw - minimal length

e.	Digital VOM

3.	Select the site for the measurement:

a.	Power requirements: Provide a clean source of 115-230 VAC, 50/60 Hz, single phase circuit rated 15A minimum.

b.	Sensor element should be located near potential leaks in a quiet area or downstream from leak source in area with air movement.

c.	Sensor element should be mounted 18” - 24” above the floor for halocarbons and near the ceiling for ammonia.

d.	Make sure the area selected is not subject to flooding, potential impact or severe ambient temperature and humidity changes (i.e. boiler blow-down or near roll-up doors).

IMPORTANT

SENSOR ELEMENT CAN BE DESTROYED BY IMMERSION IN LIQUIDS OR EXPOSURE TO SILICONE.  COVER SENSOR WITH A PLASTIC BAG WHEN SILICONE VAPORS ARE PRESENT IN MONITORED AREA.  IMMERSION OR SILICONE EXPOSURE INVALIDATES SENSOR LIFE WARRANTY.

e.	Halocarbon and LFL Sensor will respond to presence of alcohol, hydrogen, carbon monoxide, paint thinner, and many toxic and combustible gases.  For accurate refrigerant leak detection select a location free from above fumes or temporarily disable sensor as above when they are present.

4.	The wall mounted controller should be installed indoors, approximately five feet above the floor (or at a location easily visible to operators), in an area with minimal vibration, and with temperature and humidity changes like sensor location.

IMPORTANT

CONSULT LOCAL AND NATIONAL ELECTRICAL CODES FOR ANY SPECIAL REQUIREMENTS OR RESTRICTIONS BEFORE INSTALLING HALOGUARDTM.

5.	Selectors, LCD/LED Displays, and Relays

a.	AUTO/MAN Push-button - In the AUTO mode, the HaloguardTM II automatically scans all active channels in sequence.  Manual mode is initiated by pushing the MAN push-button.  In the MAN mode, monitor remains locked in a single channel until manually sequenced to another channel, by pushing MAN push-button.  After 2 minutes, sequencer will automatically default to AUTO mode.

b.	ZERO Push-button - Reads sensor output and sets this value equal to “zero” ambient condition.  ZERO function is inactive when in ANY alarm condition or during RESET (See Calibration 3c).

c.	OFFSCALE Alarm LED and Relay - Factory set at a value 2 - 3 times the full scale.

d.	HI Alarm LED/LO Alarm LED and Relays - User adjustable 10% to 100% of Full-scale value (See Calibration 4.0).

Note: Optional TWA Integration activates LOW Alarm LED and relay when installed.

e.	FAULT Alarm LED and Relay - Indicates power failure, out of calibration or sensor failure.

f.	POWER - Green LED indicates Haloguard TM is receiving power.

g.	RESET - Green LED indicates Haloguard TM in 20 minute RESET mode.  During RESET mode all alarm relays, audible and visual alarms are disabled.

10 1/2”

7 1/8”

4 1/4”

HALOGUARD II CONTROLLER

Figure 1 - Dimensional Drawing

AN1

AN2

AN3

AN4

BRIGHTNESS

JP9

RESET

MAN

ZERO

TEST

RESET

FAULT

JP1

JP2

JP3

JP4

JP5

JP6

JP7

JP8

POWER

LOW

HIGH

MICROPROCESSOR

DISPLAY

LED

PUSH-BUTTON

OFF SCALE

Figure 2 - Upper Circuit Board

T1  T2  T3

T1  T2  T3

T1  T2  T3

T1  T2  T3

T1  T2  T3

T1  T2  T3

Figure 3 - Lower Circuit Board

Figure 4 - Junction Box Relay

Figure 5 - LCD Display Features

INSTALLATION

1.	Check power supply. (See Section “Before Installation 3a”)

2.	Disconnect power before beginning.

3.	To mount HaloguardTM controller:

a.	Install No. 10 x 1” screw (minimum) wall fastener at approximate center of desired location. Slip controller over  fastener.

b.	Remove lower cover from controller to expose lower circuit board.  Install two additional fasteners through holes provided beneath lower cover.

c.	Replace cover.

4.	Mount sensors in a VERTICAL DOWN position (Oxygen sensors MUST be in vertical down position to operate properly) on indoor surface with mounting clip provided or in duct work if provided with mounting flange.  Run cable to controller location.  Eight feet (8ft.) of cable with DIN connectors standard;  optional extension cables are available.

Refer to FIGURE 3 Lower Circuit Board before proceeding.

DO NOT CUT SUPPLIED CABLE

Maximum Extension wire 300 Feet.

a.	Controller is provided with 18” cable with DIN Connector and sensor is provided with 6 1/2’ cable.  If cable extension is provided by customer, proceed as follows:

We recommend 3 conductor 18 ga. cable with foil shield, Carol C0455 or equal.  Use 3/4” conduit if required.

To extend sensor beyond the provided length, remove 18” cable with DIN connector from controller Lower Circuit Board. Splice or solder extension cable to end of 18” cable.  Reconnect extended sensor cable to proper terminal block in lower circuit board of controller. Start with Channel 1 and connect in sequence until all are connected as follows:

| Terminal | Provided Wire Color | Extension Wire Color | Function |
| --- | --- | --- | --- |
| T1 | Red | Red | VDC |
| T2 | White | White | Signal |
| T3 | Blk./Blk | Black | Ground |

Figure 6 - Terminal Connection

6	Set HI/LO ALARM jumpers for each sensor at 10. (See Figure 3 and 8 for Lower Circuit Board settings).

7	Remove cover and face plate from controller using nut driver; remove junction box cover.

Refer to Figures 2,3,and 4 before proceeding

**WARNING**ANALOG OUTPUT IS A DRIVEN SIGNAL-DO NOT CONNECT ANY WIRE  WITH 			    VOLTAGE OR CURRENT TO ANALOG OUTPUT TERMINALS

8	Connect alarm relays (NO or NC) and analog outputs AN 1 thru 4 ((+) SIG and (-) GND if supplied) where indicated. READ WARNING LAST PAGE

9	Connect power (Connect optional battery back-up if supplied.)

10. For 20 min. after initial power up all alarm relays and audible are automatically disabled. During initial power up RESET LED will be lit.  Whenever power is disrupted, RESET MODE will be automatic (unless equipped with battery back-up) to protect against false alarms.

Due to variations in the ambient (temp. and R.H.) zero calibration must be initially and periodically checked to assure best performance.  (See Calibration Section)

11.LocateSETUP jumpers JP-1 thru 9 on Upper Circuit Board.  Select required settings from the following menu:

| JP | FUNCTION |
| --- | --- |
| JP-1 | In house ONLY. |
| JP-2 | Optional AutoCalibration (See 12a) |
| JP-3 | Set scan rate, 0-10 sec. adjustable (See 12b) |
| JP-4 | Set gas type and channel (See 12c) |
| JP-5 | In House Use ONLY. System set-up info. |
| JP-6 | Set Clock, optional TWA only (See 12d) |
| JP-7 | In House Use ONLY. (Contact mfg. for changes) |
| JP-8 | Relay Latch (See 12e) |
| JP-9 | Optional Audible alarm and jumper storage.(See 12f) |

Figure 7 - Function Jumper Settings

12.After selecting from the above, the LCD will show a new mode (SETUP, etc.) and the MAN and ZERO push-buttons will have new functions.

a.	AutoCalibration (Optional) select JP-2, LCD shows ACON.  HaloguardTM compares temp. and RH every 4 hours to compensate for changes in ambient.

b.	Scan Rate - Rate is factory set at 4 sec. per active channel.  To change, select JP-3, push ZERO and step to desired rate.  Remove jumper from JP-3.

Refer to figure 5 before proceeding

c.	Channel and Gas Type - See initial factory setting chart for channel set-up  To change, select JP-4, push ZERO and sequence to channel (1 thru 6) desired, push MAN to initiate gas type menu, push ZERO and scroll to gas type desired (Note: “None” selected will skip channel).  Proceed to next channel and follow same process.  When finished, remove jumper from JP-4.

d.	TWA Integration, (Optional). HaloguardTM  calculates an 8 hr. TLV-TWA, displays this value on LCD, activates LO alarm LED and relay if preprogrammed PPM value is exceeded. (Must be powered up for 8 hrs. to build data base before operating).

e.	Relay Setup - Factory setting is Unlatched Mode; The alarm LEDs and relays will return to a normal status when gas concentration goes below setpoint.  To select Latched Mode place jumper on JP-8.  Press RESET button to release alarm or check for false alarm (Note: Alarm will be disengaged for 20 minutes).

f.	Audible Alarm - JP-9 is factory installed to activate alarm circuit.  To silence alarm remove JP-9 jumper.

12.	Trim Optional analog outputs by pushing TEST button and turning potentiometers on AN 1 thru 4  (see Figure 2 Upper Circuit Board) until output measures 5.0 or 10.0 VDC as required.

CALIBRATION

1.	The HaloguardTM has been factory calibrated under standard conditions (70oF, 65% R.H.).  Due to variations in the ambient (temp. and R.H.) zero calibration must be initially and periodically checked to assure best performance.

2.	The HaloguardTM should be powered up (operated continuously) for 24 hours before calibration.

Remove Alarm Setpoint Jumper from all active channels before beginning calibration.

3.	Calibrate with a digital VOM as follows:

HALOCARBON AND LFL SENSORS “ZERO” CALIBRATION

ZERO CALIBRATION MUST BE COMPLETED FOR EACH SENSOR

(1 thru 6)

a.	With VOM on 1 VDC scale, place VOM probe on T2 (+) and T3 (-) Test points (see Figure 3 Lower Circuit Board).

Select MAN mode with push-button, sequence to first channel.  Adjust potentiometer to the left of the terminals with screwdriver until it reads 1.0 VDC. Push ZERO.  Sequence to subsequent active channels and follow same procedure for each channel. Haloguard TM automatically returns to scanning mode after 2 minutes or press TEST button to start scanning.

Note: Zero calibration is not necessary for oxygen sensors.

b.	LCD display adjustment  changes brightness - Adjust potentiometer (See Figure 2 Upper Circuit Board).

4.	Alarm Setpoints Adjustment - (See Figure 3 - Lower Circuit Board)  Place jumper on appropriate alarm point to initiate visual and audible alarm relays.

| Jumper Settings |  | Range | Range |
| --- | --- | --- | --- |
| Low/High |  | 0 - 300 | 0 - 1000 |
| 10 |  | 300 | 1000 |
| 9 |  | 270 | 900 |
| 8 |  | 240 | 800 |
| 7 |  | 210 | 700 |
| 6 |  | 180 | 600 |
| 5 |  | 150 | 500 |
| 4 |  | 120 | 400 |
| 3 |  | 90 | 300 |
| 2 |  | 60 | 200 |
| 1 |  | 30 | 100 |

Figure 8 - Alarm Jumper Settings

| GAS | TLV-TWA* | CEIL | PEL |
| --- | --- | --- | --- |
| R-11 |  | - 1000 |  |
| - R-12 | - 1000 |  | - 1000 |
| - R-22 | - 1000 |  | - 1000 |
| - R-123 | - 50 |  |  |
| - R-134a | - 1000 |  | - 1000 |
| - R-500 | - 1000 |  | - 1000 |
| - R-502 | - 1000 |  |  |

Other exposure limits are pending.

TLV-TWA = 8hr./day, 40hr./wk. avg.  Short term exposures should not exceed 3 - 5 times the TWA for more than 30 min./day.

* ACGIH Trademark.

Figure 9 - Exposure Limits

Oxygen alarms are preprogrammed at 19.5% (LO) and 15% (HI);

(Optional) TWA Intregation, LO alarm is pre-programmed to the TLV-TWA for specified gas. Off Scale  - Preprogrammed at 2 - 3 times full scale.

SPAN CALIBRATION

Span calibration is not required for operation in typical machine room environments.  Optional Span Gas Calibration Kits are available upon request.  Instructions for calibration are included with kit.

TESTING

1.	The Haloguard TM should be tested periodically and 30 minutes after each alarm level condition has been corrected.

a.	Alarm Test - Push and hold TEST button; alarm relays, lights, audible and remote

alarms (if equipped) will activate.  Analog outputs will go full scale.

b.	Reset Test - Push RESET button; alarm relays, audible and remote alarms (if equipped) will become inactive for 20 minutes.  RESET LED will be green.

TROUBLESHOOTING

The most frequent cause of nuisance alarms is improper set-up, primarily due to:

a.	Too short a warm-up time before Zero Calibration.

b.	Poor sensor location.

To check Zero Calibration, fill a clean plastic trash bag with clean outside air, tie off  with twist-tie, let sample stabilize inside for 15 - 20 minutes, and insert sensor into bag.

Follow Zero procedures under “Calibration” Section.  Remove sensor from bag and observe LCD response.

If  PPM then moves higher, look for possible sources of interfering gases  (See “Before Installation” section 3e). and relocate sensor.

We wish to aid with any  problems you might experience with the HaloguardTM line of products.  When contacting Thermal Gas Systems, Inc. Service Department, your assistance is requested to provided the following information.

1.	Model Number and Serial Number.

2.	Description of problem.

3.	Remove faceplate from Upper and Lower Circuit Board (Figures 2 and 3) .  Advise jumper positions.

4.	Remove Junction Box cover (Figure 4).  Advise where Alarm wires are connected.

5.	Using (Figure 3  Lower Circuit Board) as a guide, measure voltage between +V and GND.; SIG and GND, for all active sensors.  Write down values.

6.	Using LCD Display (Figure 5) as a guide, observe the LCD as it scrolls.  Write down values.

7.	Advise the condition of all LED’s on the faceplate.

SPECIFICATIONS

Technology:	CMOS - Ceramic Metal Oxide 	Semiconductor

Oxygen - Electro Chemical

Electrical Supply:	115-230 VAC, 50-60Hz

Output Signal:	Std.  4 x  3A Dry Contact Relays

(either NO or NC)

Opt.  4 x 0 - 5 VDC Analog

Alarm Outputs:	Three Level Contact Closure

Readout:	Digital Meter, Displayed in PPM

Gas Type, Range and options.

Accuracy:	10% Full Scale (CMOS)

1%  Electrochemical (Oxygen)

Ranges:	0 - 1000 ppm    CFC, HCFC, HFC

0 -   300 ppm    NH3,, HCFC (Opt)

0 - 20% LFL Flammability

0 - 25% Oxygen

Response Time:	< 1 Minute per sample point

Operating Conditions:

CMOS Sensor	-20oF to +120oF Non-condensing

Oxygen Sensor	+40oF to +110oF Non-condensing

Controller	 0oF to +120oF Non-condensing

Fault Diagnostics:	Indicator Light or Readout for

Malfunction which include:

(See Figure 5)

Materials:

Controller	Polystyrene,  NEMA 12/13, IP65 Design

CMOS Sensor	PVC and porous PP

Weight:

Controller:	4 lbs. (Add 2 lbs. optional battery)

Dimensions:

Controller	10-1/2” W x 7-1/8” H x 4-1/4”D

Initial factory settings are:

| Channel | 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- | --- |
| Gas |  |  |  |  |  |  |
| Sensor Type |  |  |  |  |  |  |
| Full Scale PPM |  |  |  |  |  |  |
| TWA Alarm Level |  |  |  |  |  |  |

Figure 10 - Initial Factory Settings

GLOSSARY

| 1. | PEL- Permissable Exposure Limits - The employee’s average short term exposure in any 8-hr work shift, which shall not be exceeded. |
| --- | --- |
| 2. | CONTROLLER - Processor mounted on wall which includes LCD Display, LED Alarms Relays, and other functions |
| 3 | CEIL-The concentration that shall not be exceeded during any part of the work day. |
| 4. | SPAN - A full-scale reading on the LCD display. |
| 5. | TLV-TWA - The time -weighted average concentration for a normal 8 hr. work day and a 40 hr. work week, to which nearly all workers may be repeatedly exposed, day after day, without adverse effect. |
| 6.. | ZERO - An indication on the display indicating the presence or non-presence of CFC’s, HCFC’s or HFC’s. |