+     -

1    2

AN1

+     -

1    2

AN2

+     -

1    2

AN3

+     -

1    2

AN4

ANALOG OUTPUTS

TO BAS OR OTHER

(Typical 4)

1   NC

2   COM

3   NO

4   NC

5   COM

6   NO

7   NC

8   COM

9   NO

10  NC

11  COM

12  NO

1

2

3

4

5

6

7

8

9

10

11

12

+V S G

1  2  3

+V S G

1  2  3

+V S G

1  2  3

+V S G

1  2  3

+V S G

1  2  3

CHANNEL 1

CHANNEL 2

CHANNEL 3

CHANNEL 4

CHANNEL 5

CHANNEL 6

+V S G

1  2  3

+

-

(Optional)

BATTERY

BACK-UP

Plug in Molex Connector

J2

Line Cord 115 VAC 50/60Hz.

AC HOT

G

N

L

AC COMMON

GROUND

Green

White

Black

WARNING

Analog output lines must not be connected to any kind of voltage or current source, serious damage will result.

Notes:

1. Power Cord - Provided w/ wall plug connector and 8 Ft. 3 conductor wire.

2. Optional Audible Alarm factory wired.  Remote Audible and Visual Alarms

must be 120VAC and connected to terminal in Junction Box.

3.  Sensor Cable Use, 3 conductor 18 or 20ga. w/ foil shield.

4. Analog Outputs are either 0 - 5VDC or  0 - 10VDC.

VIS

8’ Cable w/ DIN Plug in Connector

(Typical for up to six (6) Sensors

CMOS, Oxygen)

OFFSCALE

HI ALARM

LOW ALARM

FAULT

CMOS OR OXYGEN SENSORS

MAXIMUM WIRE LENGTH 300 FT.

Figure 10 - Wiring  Diagram

(OPTIONAL)

AUDIBLE ALARM

AUD

-     +

2    1

-     +

2    1

(OPTIONAL)

STROBE ALARM

12VDC