Notes:

1. 8 ft. power  cord  provided w/ wall plug connector .

2. Local  Audible /Strobe factory wired.  Remote Audible / Visual Alarms

must be 120VAC and connected to terminal in Relay Junction Box.

3. Sensor  cable is  3 conductor 18 ga. w/ foil shield.

4. Analog Outputs are adjustable  0 - 5VDC  or  0 - 10VDC.

8’ Cable w/ DIN Plug in Connector

(Typical for up to six (6) Sensors

IR Sensor Module, or Oxygen)

OPTIONAL ANALOG OUTPUTS TO BAS OR OTHER(Typ of 4)

Line Cord

120-230VAC   50/60Hz.

(OPTIONAL)

12V AUDIBLE ALARM

(OPTIONAL) STROBE ALARM

12VDC

Cable to

IR Sensor Module

Line Cord

120-230VAC

50/60 Hz

Cable from controller, maximum length 1000 ft.

Controller

IR Sensor module

6.5”Wx14.3”Hx4.0”D

Outputs

(4) relay

contacts

3 ft. of 1/8” tubing and end of line filter provided for each IR module. Maximum extrension 200 ft. of 1/8” tubing

OFFSCALE              POWER

HI ALARM              TEST

LO ALARM             ZERO

FAULT                MAN

RESET                 RESET

Locate sample point 18-24” AFF

Haloguard II/IR  Controller

10.5”Wx7.1”Hx5.7”D

PPM-%O2