To: 									Date:

AT:

FAX:

From:

Subject:  Haloguard II/IR Model 					S/N

Message:	Please provide the following information so that we may determine the solution to your problem.

1- Describe the problem:

2- Refer to Figure 5.   Observe the LCD on Haloguard II Controller.  Provide information from each screen as it scrolls.

3-	Advise status of all the LEDs on the faceplate:

4-	Remove the faceplate; Using Figure 2 as a guide, circle which positions have jumpers installed JP-1 thru JP-9.

| JP-1 | JP-2 | JP-3 | JP-4 | JP-5 | JP-6 | JP-7 | JP-8 | JP-9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ON | ON | ON | ON | ON | ON | ON | ON | ON |
| OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF |

5-  Using Figure 2 as a guide put jumper on JP5, record all information displayed:_________

_________________________________________________________________________

_________________________________________________________________________

Figure 2 - Haloguard II Controller Upper Circuit Board

RUN

GAS

ALARM

ZERO

SPAN

AUD

J5

UP

ENTER

DOWN

AN1

AN2

AN3

AN4

BRIGHTNESS

JP9

RESET

MAN

ZERO

TEST

RESET

FAULT

JP1

JP2

JP3

JP4

JP5

JP6

JP7

JP8

POWER

LOW

HIGH

MICROPROCESSOR

DISPLAY

LED

PUSH-BUTTON

OFF SCALE

T1  T2  T3

T1  T2  T3

T1  T2  T3

T1  T2  T3

T1  T2  T3

T1  T2  T3

Figure 3 - Haloguard II Controller Lower Circuit Board

6-	Using Figure 3 as a guide, measure voltage between +V and GND, also between SIG and GND.  at terminals T1 thru T3.  Record values to the nearest millivolt (0.001V) for each sensor.  Record alarm jumper settings.

| CHANNEL | 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- | --- |
| +V & GND |  |  |  |  |  |  |
| SIG & GND |  |  |  |  |  |  |
| Low Alarm |  |  |  |  |  |  |
| High Alarm |  |  |  |  |  |  |

7-	Remove the Junction Box cover. Using Figure 4 as a guide advise wire terminations.

Figure 4 - Junction Box Relay

Lower Circuit Board

IR Module Run/

Setup Jumper

Run

Setup

DO NOT ADJUST POTS

Figure 7 - IR Sensor Module Circuit Boards

Cable to Controller

(DO NOT REMOVE)

White

Black

Red

At the IR Sensor Module

8-	Open the IR Sensor Module.  Using Figure 7, move jumper from RUN to SETUP.

9-	Examine the condition of clear plastic tubing inside the IR Sensor Module.  Make sure tubing has not detached from fittings.

At Haloguard II Controller

10-	Wait at least one minute, then Repeat Step 6 Above.  Using Figure 3 as a guide, measure voltage between +V and GND, also between SIG and GND.  at terminals T1 thru T3.  Record values to the nearest millivolt (0.001V) for each IR Sensor Module.

| CHANNEL | 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- | --- |
| +V & GND |  |  |  |  |  |  |
| SIG & GND |  |  |  |  |  |  |

11-  Refer to Figure 5.   Observe the LCD on Haloguard II Controller.  Provide information from each screen as it scrolls.

At the IR Sensor Module

12-	Move jumper from SETUP to RUN.  Close the IR Sensor Module.

The complete instruction manual may be helpful.  If a copy is required, please let me know.