OXYGUARD

SYSTEM LAYOUT

Oxyguard

Controller

5.5”Wx9.0”Hx4.0”D

Power Supply

12 VDC

50/60Hz.

POWER         ALARM 1

FAULT           ALARM 2

RESET              TEST

% Oxygen

8’ Cable w/ DIN plug provided

Outputs

(2) Relay Contacts

(1)  0 - 5 VDC or 4-20mA(optional)

Maximum extension 200 FT. Use min.18 ga

3 cond.w/foil shield

Locate sensor

18-24” AFF